## BOQ-OPT1-CAPEX
MAHINDRA WORLD CITY - JAIPUR
BILL OF QUANTITIES - OPTION 1 - CAPEX
Sr. No. | Description | Unit | Quantity | Rate (INR) | Amount (INR)
1 | SOLAR PV (CAPEX MODEL) - SYSTEM COST:
1.1 | Design-Build, procurement, fabrication, testing, supply, delivery, onsite & offsite storing, handling, hoisting, site equipment, site survey & settings, installation, testing, commissioning, removal of waste & packing, incidental charges, protection, cleaning and handover of all components of the custom designed Solar PV system, including but not limited to Solar PV modules in array panels, mounting structure, DC & AC Isolators, Inverter, Distribution Board with all accessories like busbars, neutral Links, earth Link, PPI bus links, cable end box, spreaders, per phase isolation kits, blank plates, interconnections, connectors, cable ties, angle supports for installations, required cabling with terminations, cable trays, structural supports and cable supports, cable tags, all clamping material, compression glands, lugs, hardware, earthing system, etc. complete as per schematic drawing, relevant standards & including all accessories as per site conditions to make the system fully operational. (As per applicable BIS / Equivalent IEC Standard Or MNRE specifications).
The tenderer should fully comply with the tender specifications, tender drawings & contract conditions. Tenderer should also comply with all local regulations and guidelines, any changes in the design that will be required to meet the regulations should be highlighted before the award of tender.
No variations will be allowed for any changes needed in the design to comply with local statutory requirements. The Tenderer must submit their design calculation & preliminary drawings along with the tender submission for review and approval by the Developer's in-house Design team.
Bill of quantities, description in the BOQ is indicative and the tenderer shall be responsible to read the BOQ description in conjunction with technical specifications, tender drawings, architectural drawings and any changes will not allow the tenderer to claim extra on the rates quoted. All rates shall be quoted after site visit and actual measurements at site.
Detailed calculations, shadow analysis must be provided by the tenderer along with the tender submission. Capacities indicated in the BOQ are theoretical and are not to be used for production / procurement of any material. The Tenderer must verify the capacity against drawings, calculations, site measurement from site visits and schedule for procuring the material.
Tenderer shall be responsible for the protection of his works and materials from delivery to site, during storage, progress of the site works and after installation until the works are handed over to the Developer. The Tenderer shall be responsible for the programming of his works and the coordination of his works with other trades and Tenderers.
Tenderer should have setup of off-site factory for fabrication of works available up to the completion of project and limited space shall be provided at site to carry out minor works only. Tenderer shall note that the space for storage at the site is limited and phased delivery of material to site shall be taken into consideration to avoid congestion. Tenderer shall arrange temporary storage offsite and within allocated space on site.
The quoted rate shall include all design, engineering & shop drawing approval from MLDL design team. The quote rate shall include all taxes, duties, statutory obligations and safety code compliances. Tenderer shall submit a warranty of 24 months for the entire system and back-to-back guarantee from all manufacturers of individual components. Any other material / labour / approvals required to complete the system and make it fully functional is part of this tender scope.
The rate shall include complete liaison co-ordination for net metering if required, including procurement of meter from supply authority, replacement of old meter (if any), testing and commissioning of solar PV system with net metering as applicable and handing over after generation of first net metering bill.
Tenderer's scope also includes: 1. Complete SLD from solar panel to end user load which is to be connected on solar energy 2. Identification of dedicated load to be put on solar energy if any with respect to Developer's electrical SLD 3. Plan Layout with space planning for net meter as applicable & generation meter installation including CTs 4. Schedule of work or SOP to be provided post installation of solar panel with Inverter 5. Earthing & lightning protection for entire Solar PV Plant 6. Handing over of the solar system with net meter & generation meter as applicable to be coordinated with service provider post first net metering electricity bill. 7. Making As-built drawing after completion of work.
1.1.1 | Solar PV System - MWCJ: a) MTP evolve (290 kW) + b) IT UGR (81 kW) = 2150 SFT Terrace area c) UGR-DTA (40 kW) = 1300 SFT Terrace area d) STP-DTA (61 kW) = 12.82 SFT Terrace area e) STP, UGR & TTP HC (135 kW) = 1650 SFT Terrace area Date of commencement: Immediate, Duration for completion: 3 months from commencement date | SET | 1 |  | 0
2 | SOLAR PV (CAPEX MODEL) - MAINTENANCE COST:
2.1 | OPTION 1 - NON-COMPREHENSIVE ANNUAL MAINTENANCE:
Detailed scope of AMC shall be as per annexure attached with the Tender. Payment of AMC services shall be on quarterly basis after completing maintenance of the quarter, within 30 days from bill submission date.
2.1.1 | YEAR 1: During 1st year of DLP | YEAR | 1 |  | 0
2.1.2 | YEAR 2: During 2nd year of DLP | YEAR | 1 |  | 0
2.1.3 | YEAR 3: 1st year after DLP | YEAR | 1 |  | 0
2.1.4 | YEAR 4: 2nd year after DLP | YEAR | 1 |  | 0
2.1.5 | YEAR 5: 3rd year after DLP | YEAR | 1 |  | 0
2.2 | OPTION 2 - COMPREHENSIVE ANNUAL MAINTENANCE:
Detailed scope of AMC shall be as per annexure attached with the Tender. Payment of AMC services shall be on quarterly basis after completing maintenance of the quarter, within 30 days from bill submission date.
2.2.1 | YEAR 1: During 1st year of DLP | YEAR | 1 |  | 0
2.2.2 | YEAR 2: During 2nd year of DLP | YEAR | 1 |  | 0
2.2.3 | YEAR 3: 1st year after DLP | YEAR | 1 |  | 0
2.2.4 | YEAR 4: 2nd year after DLP | YEAR | 1 |  | 0
2.2.5 | YEAR 5: 3rd year after DLP | YEAR | 1 |  | 0

## BOQ-OPT2-OPEX
MAHINDRA WORLD CITY - JAIPUR
BILL OF QUANTITIES - OPTION 2 - OPEX
Sr. No. | Description | Unit | Quantity | Rate (INR) | Amount (INR)
1 | SOLAR PV (OPEX MODEL FOR 10 YEARS) - SYSTEM COST:
1.1 | Design-Build, procurement, fabrication, testing, supply, delivery, onsite & offsite storing, handling, hoisting, site equipment, site survey & settings, installation, testing, commissioning, operation & maintenance, removal of waste & packing, incidental charges, protection, cleaning and handover of all components of the custom designed Solar PV system, including but not limited to Solar PV modules in array panels, mounting structure, DC & AC Isolators, Inverter, Distribution Board with all accessories like busbars, neutral Links, earth Link, PPI bus links, cable end box, spreaders, per phase isolation kits, blank plates, interconnections, connectors, cable ties, angle supports for installations, required cabling with terminations, cable trays, structural supports and cable supports, cable tags, all clamping material, compression glands, lugs, hardware, earthing system, etc. complete as per schematic drawing, relevant standards & including all accessories as per site conditions to make the system fully operational. (As per applicable BIS / Equivalent IEC Standard Or MNRE specifications).
The tenderer should fully comply with the tender specifications, tender drawings & contract conditions. Tenderer should also comply with all local regulations and guidelines, any changes in the design that will be required to meet the regulations should be highlighted before the award of tender.
No variations will be allowed for any changes needed in the design to comply with local statutory requirements. The Tenderer must submit their design calculation & preliminary drawings along with the tender submission for review and approval by the Developer's in-house Design team.
Bill of quantities, description in the BOQ is indicative and the tenderer shall be responsible to read the BOQ description in conjunction with technical specifications, tender drawings, architectural drawings and any changes will not allow the tenderer to claim extra on the rates quoted. All rates shall be quoted after site visit and actual measurements at site.
Detailed calculations, shadow analysis must be provided by the tenderer along with the tender submission. Capacities indicated in the BOQ are theoretical and are not to be used for production / procurement of any material. The Tenderer must verify the capacity against drawings, calculations, site measurement from site visits and schedule for procuring the material.
Tenderer shall be responsible for the protection of his works and materials from delivery to site, during storage, progress of the site works and after installation until the works are handed over to the Developer. The Tenderer shall be responsible for the programming of his works and the coordination of his works with other trades and Tenderers.
Tenderer should have setup of off-site factory for fabrication of works available up to the completion of project and limited space shall be provided at site to carry out minor works only. Tenderer shall note that the space for storage at the site is limited and phased delivery of material to site shall be taken into consideration to avoid congestion. Tenderer shall arrange temporary storage offsite and within allocated space on site.
The quoted rate shall include all design, engineering & shop drawing approval from MLDL design team. The quote rate shall include all taxes, duties, statutory obligations and safety code compliances. Tenderer shall submit a warranty of 24 months for the entire system and back-to-back guarantee from all manufacturers of individual components. Any other material / labour / approvals required to complete the system and make it fully functional is part of this tender scope.
The rate shall include complete liaison co-ordination for net metering if required, including procurement of meter from supply authority, replacement of old meter (if any), testing and commissioning of solar PV system with net metering as applicable and handing over after generation of first net metering bill.
Tenderer's scope also includes: 1. Complete SLD from solar panel to end user load which is to be connected on solar energy 2. Identification of dedicated load to be put on solar energy if any with respect to Developer's electrical SLD 3. Plan Layout with space planning for net meter as applicable & generation meter installation including CTs 4. Schedule of work or SOP to be provided post installation of solar panel with Inverter 5. Earthing & lightning protection for entire Solar PV Plant 6. Handing over of the solar system with net meter & generation meter as applicable to be coordinated with service provider post first net metering electricity bill. 7. Making As-built drawing after completion of work.
1.1.1 | Solar PV System - MWCJ: a) MTP evolve (290 kW) + b) IT UGR (81 kW) = 2150 SFT Terrace area c) UGR-DTA (40 kW) = 1300 SFT Terrace area d) STP-DTA (61 kW) = 12.82 SFT Terrace area e) STP, UGR & TTP HC (135 kW) = 1650 SFT Terrace area Date of commencement: Immediate, Duration for completion: 3 months from commencement date | Per Unit |  |  | 0
2 | SOLAR PV (OPEX MODEL FOR 10 YEARS) - BUY OUT VALUE:
Buy out value for Solar PV system (OPEX MODEL)
2.1 | YEAR 1 | YEAR | 1 |  | 0
2.2 | YEAR 2 | YEAR | 1 |  | 0
2.3 | YEAR 3 | YEAR | 1 |  | 0
2.4 | YEAR 4 | YEAR | 1 |  | 0
2.5 | YEAR 5 | YEAR | 1 |  | 0
2.6 | YEAR 6 | YEAR | 1 |  | 0
2.7 | YEAR 7 | YEAR | 1 |  | 0
2.8 | YEAR 8 | YEAR | 1 |  | 0
2.9 | YEAR 9 | YEAR | 1 |  | 0
2.1 | YEAR 10 | YEAR | 1 |  | 0

## BOQ-OPT3-OPEN ACCESS
MAHINDRA WORLD CITY - JAIPUR
BILL OF QUANTITIES - OPTION 3 - OPEN ACCESS
Sr. No. | Description | Unit | Quantity | Rate (INR) | Amount (INR)
1 | SOLAR PV (OPEN ACCESS MODEL) - SYSTEM COST:
1.1 | Design, procurement, fabrication, testing, onsite & offsite storing, handling, hoisting, site equipment, site survey & settings, installation, testing, commissioning, operation & maintenance, removal of waste & packing, incidental charges, protection, cleaning and handover of all components of the custom designed Solar PV system at an open access solar farm, including but not limited to Solar PV modules in array panels, mounting structure, DC & AC Isolators, Inverter, Distribution Board with all accessories like busbars, neutral Links, earth Link, PPI bus links, cable end box, spreaders, per phase isolation kits, blank plates, interconnections, connectors, cable ties, angle supports for installations, required cabling with terminations, cable trays, structural supports and cable supports, cable tags, all clamping material, compression glands, lugs, hardware, earthing system, etc. complete as per schematic drawing, relevant standards & including all accessories as per site conditions to make the system fully operational. (As per applicable BIS / Equivalent IEC Standard Or MNRE specifications).
The tenderer should fully comply with the tender specifications, tender drawings & contract conditions. Tenderer should also comply with all local regulations and guidelines, any changes in the design that will be required to meet the regulations should be highlighted before the award of tender.
No variations will be allowed for any changes needed in the design to comply with local statutory requirements. The Tenderer must submit their design calculation & preliminary drawings along with the tender submission for review and approval by the Developer's in-house Design team.
Bill of quantities, description in the BOQ is indicative and the tenderer shall be responsible to read the BOQ description in conjunction with technical specifications, tender drawings, architectural drawings and any changes will not allow the tenderer to claim extra on the rates quoted. All rates shall be quoted after site visit and actual measurements at site.
Detailed calculations, shadow analysis must be provided by the tenderer along with the tender submission. Capacities indicated in the BOQ are theoretical and are not to be used for production / procurement of any material. The Tenderer must verify the capacity against drawings, calculations, site measurement from site visits and schedule for procuring the material.
Tenderer shall be responsible for the protection of his works and materials from delivery to farm site and from farm site to MLDL project, during storage, progress of the site works and after installation until the works are handed over to the Developer. The Tenderer shall be responsible for the programming of his works and the coordination of his works with other trades.
Tenderer should have setup of off-site factory for fabrication of works available up to the completion of project and limited space shall be provided at site to carry out minor works only. Tenderer shall note that the space for storage at the site is limited and phased delivery of material to site shall be taken into consideration to avoid congestion. Tenderer shall arrange temporary storage offsite and within allocated space on site.
The quoted rate shall include all design, engineering & shop drawing approval from MLDL Design team. The quote rate shall include all taxes, duties, statutory obligations and safety code compliances. Tenderer shall submit a warranty of 24 months for the entire system and back-to-back guarantee from all manufacturers of individual components. The quoted rates shall include transmission charges, wheeling charges, transmission and wheeling losses, Cross-subsidy surcharge (CSS), Additional surcharge (AS), Banking charges, etc. Any other material / labour / approvals required to complete the system and make it fully functional is part of this tender scope.
The rate shall include complete liaison co-ordination for net metering if required, including procurement of meter from supply authority, replacement of old meter (if any), testing and commissioning of solar PV system with net metering as applicable and handing over after generation of first net metering bill.
Tenderer's scope also includes: 1. Complete SLD from solar panel to end user load which is to be connected on solar energy 2. Identification of dedicated load to be put on solar energy if any with respect to Developer's electrical SLD 3. Plan Layout with space planning for net meter as applicable & generation meter installation including CTs 4. Schedule of work or SOP to be provided post installation of solar panel with Inverter 5. Earthing & lightning protection for entire Solar PV Plant 6. Handing over of the solar system with net meter & generation meter as applicable to be coordinated with service provider post first net metering electricity bill. 7. Making As-built drawing after completion of work.
1.1.1 | Solar PV System - MWCJ: a) MTP evolve (290 kW) + b) IT UGR (81 kW) = 2150 SFT Terrace area c) UGR-DTA (40 kW) = 1300 SFT Terrace area d) STP-DTA (61 kW) = 12.82 SFT Terrace area e) STP, UGR & TTP HC (135 kW) = 1650 SFT Terrace area Date of commencement: Immediate, Duration for completion: 3 months from commencement date | Per Unit |  |  | 0

## BOM
MAHINDRA WORLD CITY - JAIPUR |  |  |  |  | LOCATIONS
BILL OF MATERIAL |  |  |  |  | UGR-DTA 40 kWp | STP-DTA 61 kWp | IT-UGR 81 kWp | Handicraft- 134.67 kWp | MTP - Evolve 289.77 kWp | Total 607 kWp
S. No. | Material Description | Rating / Specification | Make | UOM | Qty. | Qty. | Qty. | Qty. | Qty.
Section A | DC Supply
1 | Module | Mono perc 390 Watt and above | Approved make | No.
2 | DC cable for module to inverter | 1C X 6 sqmm (Red & Black 50% each) (Multi strands) | Polycab/ KEI/ Equivalent | No.
3 | MMS with Hardware (For RCC Roof) | Column Post - HDG, Rafter/Perlin - galvalume 1.6/0.9mm., Min. Ground clearance -500mm, Wind Speed @ 170 kM/Hrs. Module mounting hardware SS-304. Module tilt - 20 degree | JSW/Bluescope | KG
4 | MMS with Hardware (For Ground) | Column Post - HDG, Rafter/Perlin - galvalume 1.6/0.9mm., Min. Ground clearance -500mm, Wind Speed @ 170 kM/Hrs. Module mounting hardware SS-304. Module tilt - 20 degree |  | KG
5 | MC4 connector | IP - 68 | Elmex | No.
Section B | AC Supply
6 | Inverter (String) | 15 kW, 1000V DC | Sungrow | No.
7 | Inverter (String) | 20 kW, 1000V DC |  | No.
8 | Inverter (String) | 33kW, 1000V DC |  | No.
9 | Inverter (String) | 50 kW, 1000V DC |  | No.
10 | Inverter (String) | 100 kW, 1000V DC |  | No.
11 | Inverter mounting structure with canopy | GI Canopy |  | No.
12 | AC Cable for Inverter to ACDB | 3.5 C X 25 SQMM Al UnAr CABLE (1.1KV) | Polycab/ KEI/ Equivalent | Mtr
13 | AC Cable for Inverter to ACDB | 3.5 C X 35 SQMM Al UnAr CABLE (1.1KV) |  | Mtr
14 | AC Cable for Inverter to ACDB | 3.5 C X 50 SQMM Al UnAr CABLE (1.1KV) |  | Mtr
15 | AC Cable for Inverter to ACDB | 3.5 C X 70 SQMM Al UnAr CABLE (1.1KV) |  | Mtr
16 | AC Cable for Inverter to ACDB | 3.5 C X 95 SQMM Al UnAr CABLE (1.1KV) |  | Mtr
17 | AC Cable for ACDB to MDB | 3.5 C X 25 SQMM Al UnAr CABLE (1.1KV) |  | Mtr
18 | AC Cable for ACDB to MDB | 3.5 C X 150 SQMM Al Ar CABLE (1.1KV) |  | Mtr
19 | AC Cable for ACDB to MDB | 3.5 C X 185 SQMM Al Ar CABLE (1.1KV) |  | Mtr
20 | AC Cable for ACDB to MDB | 3.5 C X 240 SQMM Al Ar CABLE (1.1KV) |  | Mtr
21 | AC Cable for ACDB to MDB | 3.5 C X 300 SQMM Al Ar CABLE (1.1KV) |  | Mtr
22 | AC Cable for MDB to POC | 3.5 C X 95 SQMM Al Ar CABLE (1.1KV) |  | Mtr
23 | AC Cable for MDB to POC | 3.5 C X 150 SQMM Al Ar CABLE (1.1KV) |  | Mtr
24 | AC Cable for MDB to POC | 3.5 C X 240 SQMM Al Ar CABLE (1.1KV) |  | Mtr
25 | ACDB | 1 IN / 1 OUT IN: 1X63 Amp MCB curve C, with SPD type 2 | Schneider | No.
26 | ACDB | 1 IN / 1 OUT IN: 1X100 Amp MCCB, 25KA, with SPD type 2 | Schneider | No.
27 | ACDB | 2 IN / 1 OUT IN: 1 X 100 A MCCB, 1 X 40 A MCB 25 KA, OUT: 1X150 AMP Isolator with SPD type-2 | Schneider | No.
28 | ACDB | 2 IN / 1 OUT IN: 1 X 200 A MCCB, 1 X 32 A MCB 25 KA, OUT: 1X250 AMP Isolator with SPD type-2 | Schneider | No.
29 | ACDB | 3 IN / 1 OUT IN: 2 X 200 A MCCB, 1 X 100 A MCCB 25 KA, OUT: 1X320 AMP Isolator with SPD type-2 | Schneider | No.
30 | Main ACDB | 1 IN / 1 OUT IN: 1X63 Amp MCB curve C, with SPD type 2 and MFM. | Schneider | No.
31 | Main ACDB | 1 IN / 1 OUT IN: 1X100 Amp MCCB, 25KA, with SPD type 2 and MFM | Schneider | No.
32 | Main ACDB | 1 IN / 1 OUT IN: 1 X 150 A MCCB, with type 2 SPD and MFM | Schneider | No.
33 | Main ACDB | 1 IN / 1 OUT IN: 1 X 250 A MCCB, with type 2 SPD and MFM | Schneider | No.
34 | Main ACDB | 1 IN / 1 OUT IN: 1 X 320 A MCCB, with type 2 SPD and MFM | Schneider | No.
35 | Earthing cable (For MMS & Module) | 1C X 6 sqmm Cu Flexible (Green) | Polycab/ KEI/ Equivalent | Mtr
36 | Inverter earthing cable | 1C x 16 sqmm Cu Cable | Polycab/ KEI/ Equivalent | Mtr
37 | LA earthing cable | 1C x 50 sqmm Cu Cable | Polycab/ KEI/ Equivalent | Mtr
38 | Communication Cable | RS 485 cable |  | Mtr
39 | Cable tray | 100 X 40 X 1.6 mm | GI | Mtr
40 | Cable tray | 150 X 60 X 1.6 mm | GI | Mtr
41 | Cable Lugs | As per Site Requirement | Dowells/Equivalent
42 | Conduit Pipe | As per Site Requirement | Astral/Apollo/AKG
Section C | Earthing and Lightening Protection
43 | Earthing pit with cover frp or cast iron | 17mm dia - 3 Meter Long, Copper Bonded Rod, with Chemical Compound & Earth Pit with FRP cover plate. | Saboo/Truepower | Set
44 | LA with counter | 63 m radius ESE type | Saboo/Truepower | No.
45 | LA with counter | 107 m radius ESE type | Saboo/Truepower | No.
46 | Earthing strip for Equipment, 25 x 3 mm | 25 x 3 mm GI Strip | GI | Mtr
Section D | Safety and Fire Fighting Equipment
47 | Rubber mat | - |  | Mtr
48 | Fire Extinguisher | Minimum two numbers of fire extinguishers (CO2 and Foam type each of capacity 10 kg having BIS certification marking as per IS: 2171) shall be provided at every building/ encloser, transformer yard and switchyard. | ISI Marked | Set
49 | Sand Bucket | - |  | No.
Section E | Plant Monitoring and WMS
50 | Weather Monitoring System | With sensors for wind speed, wind direction, ambient temperature, module temperature, pyranometer andRH factor | Good Quality | Set
51 | Data - Logger | For remote monitoring | Sungrow | Set
52 | Meter | Main and Check Meter (as per requirement) with 0.5s class. | Secure | Set
53 | Meter box with CTs |  |  | Set
Section F | Civil
54 | Pile foundation for MMS (For Ground only) | Pile size - 1500 mm - depth , 300mm - dia | M20 | Nos.
Section G | Misc.
55 | Module Cleaning System | - | Manual | Set
56 | Danger Board | Size of each danger notice plates shall be 200 mm x 150 mm made of mild steel sheet and at least 2 mm thick, and vitreous enamelled white on both sides and with inscription in signal red colours on front side as required |  | No.
57 | Sign Boards | - |  | Set
Section H | Spare
58 | Spares | Quantity of Spare Modules |  | Nos.
Section I | Testing, Installation and Commissioning
59 | I & C | As per System Size |  | kW